## Definition
| NEW | ↓ | ↓ | ↓ | ↓* |  |  |  | ↓*
Macro | Used in Components / MACRO | TRNSYS Input Use | TRNSYS Input Name | TRNSYS Input equal | TRNSYS input | User Input | EXCEL Formula / Default Values Correlation | Unit | TRNSYS Formula / Default Values Correlation | Description Variable and Correlation | Interface's User | Triple Validation Check: Original Validation / TRNSYS Formula / Excel Formula | Trazability | colour code
MACRO 1300
M1300 |  | * | FLUID PARAMETERS
M1300 |  |  | EQUATION | 9 | [7 empty] | 1 | V001
M1300 |  |  | M1300_PriAntifree | = | 30 |  | 30 | % | 30 | Percentage of antifreeze | Level#2 | 1 | V001
M1300 | M1300_WSS01 M1300_PU01 M1300_PI01 M1300_PI02 M1300_HX01 |  | M1300_CpPri | = | 3.8908 |  | 3.8908 | kJ/kg.K | (4.185-M1300_PriAntifree*0.9808/100) | Fluid specific heat (primary loop) |  | 1 | V001
M1300 | M1300_PI01 M1300_PI02 |  | M1300_RoPri | = | 1014.2209 |  | 1014.2209 | kg/m3 | (1000+47.403*M1300_PriAntifree/100) | Fluid density (primary loop) |  | 1 | V001
M1300 | M1300_PI01 M1300_PI02 |  | M1300_MuPri | = | 3.2796 |  | 3.2796 | kg/m.h | 3600*(0.0005+0.0008*M1300_PriAntifree/100+0.0019*(M1300_PriAntifree/100)^2) | Fluid viscosity (primary loop) |  | 1 | V001
M1300 | M1300_PI01 M1300_PI02 |  | M1300_KPri | = | 2.2 |  | 2.2 | kJ/h.m.K | 2.2 | Fluid thermal conductivity (primary loop) |  | 1 | V001
M1300 | M1300_PU02 M1300_HX01 |  | M1300_CpSec | = | 4.19 |  | 4.19 | kJ/kg.K | CpAgua | Fluid specific heat (secondary loop) |  | 1 | V001
M1300 | M1300_PI01 M1300_PI02 |  | M1300_RoSec | = | 1000 |  | 1000 | kg/m3 | RoAgua | Fluid density (secondary loop) |  | 1 | V001
M1300 |  |  | M1300_MuSec | = | 1.8 |  | 1.8 | kg/m.h | MuAgua | Fluid viscosity (secondary loop). Not used when deleting secondary pipes. |  | 1 | V001
M1300 |  |  | M1300_KSec | = | 2.34 |  | 2.34 | kJ/h.m.K | Kagua | Fluid thermal conductivity (secondary loop). Not used when deleting secondary pipes. |  | 1 | V001
M1300 |  | * | HORIZON AND ARRAY SHADOW PARAMETERS
M1300 |  |  | EQUATION | 9 | [7 empty] | 1 | V001
M1300 | M1300_MSK01 |  | M1300_MSK_NumAngles | = |  |  | 16 | - | 16 | Number of surface angles |  | 1 | V001
M1300 | M1300_SHD01 |  | M1300_GrHrAzimuth | = |  |  | 0 | ° | 0 | Collector (¡¡¡ and Solar Field Ground !!!) Azimuth angle | Level#1 | 1 | V001
M1300 | M1300_SHD01 |  | M1300_GrHrSlope | = |  |  | 0 | ° | 0 | Ground slope versus horizontal | Level#1 | 1 | V001
M1300 | M1300_SHD01 |  | M1300_WSSHeightShadow | = | 2.427 |  | 2.427 | m | M1300_COL01_Cheight+(EQL(PAR_STC,4)+EQL(PAR_STC,7)) | WESSUN Collector Height is Solar Collector Height plus the second reflector's height only for technologies with 2R. | Level#1Ext.File Collector | 1 | V001
M1300 | M1300_SHD01 |  | M1300_WSSSlopeShadow | = | 45.001 |  | 45.001 | ° | M1300_ColHrSlope+0.001 | Collector slope (WSS) for shadows' calculation. |  | 1 | V001
M1300 |  | * | M1300_WSS01_GndUsability |  | 0.35521 |  | 0.35521 | - | M1300_WSS01_Cheight*COS(M1300_ColHrSlope)/M1300_WSSRowSep*1 | Ground usability (WSS). For M1300 internal use. |  | 1 | V001
M1300 |  | * | M1300_COL01_GndUsability |  | 0.50234 |  | 0.50234 | - | M1300_WSS01_Cheight/M1300_WSSRowSep | Ground usability (traditional collector).For M1300 internal use. |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_Cheight | = | 3.2789 |  | 3.2789 | - | (EQL(PAR_STC,1)*2.191+EQL(PAR_STC,2)*2.224+EQL(PAR_STC,3)*3.0736+EQL(PAR_STC,4)*3.9231+EQL(PAR_STC,5)*2.427+EQL(PAR_STC,6)*3.2789+EQL(PAR_STC,7)*4.1332) | Collector height used to calculate shadows and ground usability. | Level#1Ext.File Collector | 1 | V001
M1300 | M1300_SHD01 |  | M1300_WSSRowLen | = | 237.3408 |  | 237.3408 | m | MAX(60,(3*M1300_WSS01_Area)^0.5) | Collector row length. Correlation points to a square solar field with a relative row separation (to heights' collector) equal to 3 and the restriction of a minimum row width of 60 [m]. |  | 1 | V001
M1300 | M1300_SHD01 |  | M1300_WSSNRows | = | 79.1136 |  | 79.1136 | - | M1300_WSS01_Area/M1300_WSSRowLen | Number of rows equal to solar field area divided by row width (length in shadow TRNSYS type nomenclature). |  | 1 | V001
M1300 | M1300_SHD01 |  | M1300_WSSRowSep | = | 6.5273 |  | 6.5273 | m | (1+0.25*NOT(EQL(M1300_ColHrSlope,0))+0.25*(MIN(90,ABS(M1300_ColHrAzimuth))/90))*(M1300_WSSHeightShadow)*(COS(M1300_ColHrSlope)+SIN(M1300_ColHrSlope)/TAN(90-ABS(Lat)-23.5)) | Collector row separation versus horizontal. Default correlation is based on the minimum distance for 12:00 solar time winter solstice, by two additional factors. For more detailed information see M1300 Manual Description | Level#1 | 1 | V001
M1300 |  | * | COLLECTOR PARAMETERS
M1300 |  |  | EQUATION | 37 | [7 empty] | 1 | V001
M1300 | M1300_WSS01 |  | PAR_STC | = | 6 |  | 6 | - | 6 | Solar Collector Technology included in external file. By default M1300 will include 7 different solar thermal collector technologies: 1-FPC, 2-GOT, 3-GOT_WeSSun_1R, 4-GOT_WeSSun_2R, 5-LIN, 6-LIN_WeSSun_1R, 7-LIN_WeSSun_2R, | Level#1Ext.File Collector | 1 | V001
M1300 | M1300_WSS01 |  | PAR_KSOIL | = | 0 |  | 0 | - | 0 | Additional soiling factor for WESSUN reflectors |  | 1 | V001
M1300 | M1300_WSS01 |  | PAR_fRedDifusa | = | 0.8 |  | 0.8 | - | 0.8 | Concentrated diffuse radiation non-profitability factor for Reflectors. 0.2 means 80% profitability. 0.8 means 20% profitability (by default). |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_TCol_est | = | 101.5 |  | 101.5 | °C | (TDemSetpar+TDemRetpar)*0.5+M1300_HX01_DTLM+15*PAR_REN | Mean collector operation temperature. ### Only used for pre-sizing WESSUN collector area ###. |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_EFF_COL | = | 0.53718 |  | 0.53718 | % | MAX(0.3,M1300_WSS01_a0-M1300_WSS01_a1/WTOKJPH*(M1300_WSS01_TCol_est-TAirAve)/Itnom-M1300_WSS01_a2/WTOKJPH*(M1300_WSS01_TCol_est-TAirAve)^2/Itnom) | Mean collector efficiency estimation. ### Only used for pre-sizing WESSUN collector area ###. |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_Area | = | 18776.8857 |  | 18776.8857 | m2 | 0.75*QDEMMAND*PAR_REN/(((Gbh+Gdh/M1300_WSS01_C)*COS(ABS(Lat)-M1300_ColHrSlope))*M1300_EFF_COL) | WESSUN Aperture area pre-sizing based on mean collector efficiency and beam and diffuse radiation. |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_farea | = | 0.9 |  | 0.9 | - | 0.9 | WESSUN net aperture area factor. Relationship between net area and Aperture area regarding to non-useful ETC manifold-headers or PFC frames structures. |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_Areau | = | 16899.1971 |  | 16899.1971 | m2 | M1300_WSS01_Area*M1300_WSS01_farea | WESSUN net Aperture area pre-sizing based on mean collector efficiency and beam and diffuse radiation. |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_ColHrSlope | = | 45 |  | 45 | ° | 45 | Collector slope versus horizontal | Level#1 | 1 | V001
M1300 | M1300_WSS01 |  | M1300_ColHrAzimuth | = | 0 |  | 0 | ° | M1300_GrHrAzimuth | Collector (and Solar Field Ground) Azimuth angle |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_COL01_Mode | = | 2 |  | 2 | - | (EQL(PAR_STC,1)+EQL(PAR_STC,2))*1+(EQL(PAR_STC,3)+EQL(PAR_STC,4)+EQL(PAR_STC,5)+EQL(PAR_STC,6)+EQL(PAR_STC,7))*2 ! | WSS operating mode. Whether by-axial asymmetric IAM external files (mandatory for WESSUN technology) or IAM-K50 values will be used depends on this parameter. | Level#1Ext.File Collector | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_Nserie | = | 2 |  | 2 | - | MIN(M1300_WSS01_Ncol,2) | Number of collectors in series. Maximum 2 serial connection by default. |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_Nparalel | = | 1558.2478 |  | 1558.2478 | - | M1300_WSS01_Ncol/M1300_WSS01_Nserie | Number of parallel collectors |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_Acol | = | 6.025 |  | 6.025 | m2 | (EQL(PAR_STC,1)*2.52+EQL(PAR_STC,2)*12.13+EQL(PAR_STC,3)*16.764+EQL(PAR_STC,4)*21.397+EQL(PAR_STC,5)*4.46+EQL(PAR_STC,6)*6.025+EQL(PAR_STC,7)*7.595) | Collector Area (No WSS). Manufacturer data. | Level#1Ext.File Collector | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_Ncol | = | 3116.4955 |  | 3116.4955 | - | M1300_WSS01_Area/(M1300_WSS01_Acol) | Number of collectors |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_COL01_Cheight | = | 2.427 |  | 2.427 | m2 | (EQL(PAR_STC,1)*2.191+(EQL(PAR_STC,2)+EQL(PAR_STC,3)+EQL(PAR_STC,4))*2.224+(EQL(PAR_STC,5)+EQL(PAR_STC,6)+EQL(PAR_STC,7))*2.427) | Collector height.Manufacturer data. | Level#1Ext.File Collector | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_TestMode | = | 2 |  | 2 | - | 2 | Method in which the collector efficiency results are reported: 1 = As a function of the inlet temperature (common in the U.S.) 2 = As a function of the average temperature (common in Europe) 3 = As a function of the outlet temperature (common for air collectors) (2 by default). |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_ThCap | = | 68899.1344 |  | 68899.1344 | kJ/K | M1300_WSS01_ThCapUn*M1300_WSS01_Area/M1300_WSS01_C | Capacitance of Collector and the fluid it contains. |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_ThCapUn | = | 4.9573 |  | 4.9573 | kJ/K.m2 | (0.4*M1300_CpPri+0.2*9*0.82+5*0.385) | Capacitance of Collector per m2. (Fluid + Glass + Copper). To Improve por ETC |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_Reflec | = | 0.94 |  | 0.94 | % | 0.94 | Percentage of reflected radiation in WESSUN Reflectors | Level#2 | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_C | = | 1.351 |  | 1.351 | - | ((EQL(PAR_STC,1)+EQL(PAR_STC,2)+EQL(PAR_STC,5))*1+EQL(PAR_STC,3)*1.382+EQL(PAR_STC,4)*1.764+EQL(PAR_STC,6)*1.351+EQL(PAR_STC,7)*1.703) | WESSUN concentration ratio. | Level#1Ext.File Collector | 1 | V001
M1300 | M1300_WSS01 |  | M1300_COL01_a0 | = | 0.642 |  | 0.642 | - | EQL(PAR_STC,1)*0.761+(EQL(PAR_STC,2)+EQL(PAR_STC,3)+EQL(PAR_STC,4))*0.857+(EQL(PAR_STC,5)+EQL(PAR_STC,6)+EQL(PAR_STC,7))*0.642 | Tested Collector Intercept efficiency a0 | Level#1Ext.File Collector | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_a0 | = | 0.63199 |  | 0.63199 | - | M1300_COL01_a0*(1-PAR_KSOIL)*(1+M1300_WSS01_Reflec*(M1300_WSS01_C-1))/M1300_WSS01_C | WESSUN Collector Intercept efficiency a0 |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_COL01_a1 | = | 0.89 |  | 0.89 | W/m2.K | (EQL(PAR_STC,1)*3.711+(EQL(PAR_STC,2)+EQL(PAR_STC,3)+EQL(PAR_STC,4))*3.083+(EQL(PAR_STC,5)+EQL(PAR_STC,6)+EQL(PAR_STC,7))*0.89) | Tested Collector 1st order loss coefficient (a1) | Level#1Ext.File Collector | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_a1 | = | 2.3716 |  | 2.3716 | kJ/h.m2.K | M1300_COL01_a1/M1300_WSS01_C*WTOKJPH | WESSUN Collector 1st order loss coefficient (a1) |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_COL01_a2 | = | 0.001 |  | 0.001 | W/m2.K2 | (EQL(PAR_STC,1)*0.014+(EQL(PAR_STC,2)+EQL(PAR_STC,3)+EQL(PAR_STC,4))*0.013+(EQL(PAR_STC,5)+EQL(PAR_STC,6)+EQL(PAR_STC,7))*0.001) | Tested Collector 2nd order loss coefficient (a2) | Level#1Ext.File Collector | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_a2 | = | 0.0026647 |  | 0.0026647 | kJ/h.m2.k2 | M1300_COL01_a2/M1300_WSS01_C*WTOKJPH | WESSUN Collector 2nd order loss coefficient (a2) |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_Mtest | = | 50 |  | 50 | kg/h | 50 | Tested flow rate per unit area |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_COL01_IAMK50 | = | 1 |  | 1 | - | EQL(PAR_STC,1)*0.91+EQL(PAR_STC,2)*0.91+(EQL(PAR_STC,3)+EQL(PAR_STC,4)+EQL(PAR_STC,5)+EQL(PAR_STC,6)+EQL(PAR_STC,7))*1 | IAM K50 | Level#1Ext.File Collector | 1 | V001
M1300 | M1300_WSS01 |  | M1300_COL01_IAM1 | = | 0 |  | 0 | - | MAX(0,(1-M1300_COL01_IAMK50)*COS(50)/(1-COS(50))) | 1st-order IAM (b0). Only used in non-WESSUN technologies. |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_COL01_IAM2 | = | 0 |  | 0 | - | 0 | 2nd-order IAM (b1). Only used in non-WESSUN technologies. |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_DataTrans | = | 35 |  | 35 | - | 35 | Number of transverse IAM data points |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_DataLong | = | 13 |  | 13 | - | 13 | Number of longitudinal IAM data points |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_CtFRMin | = | 0 |  | 0 | kg/h | 0 | The minimum flow rate through the entire solar collector array that can be achieved when the pump is operating. |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_MPAC | = | 25 |  | 25 | kg/h.m2 | M1300_WSS01_MTest/M1300_WSS01_Nserie | The maximum flow rate through the entire collector array per unit area. | Level#1 | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_Control | = | 0 |  | 0 | - | 0 | The type of flow-control that will be used for the primary loop control: 0-Fixed Flow Rate. 1-Match-flow Rate for desired temperature T storage (x_M1300_CON02_Thigh, M1300_TAcuHigh) + 1ºC 2-Match-flow Rate for desired temperature M1300_WSS01_Tset | Level#1 | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_Tset | = | 101 |  | 101 | °C | TDemSetpar + M1300_HX01_DTLM + 2 | Desired temperature for matchflow mode M1300_WSS01_Control = 2 |  | 1 | V001
M1300 |  | * | PIPE PARAMETERS
M1300 |  |  | EQUATION | 9 | [7 empty] | 1 | V001
M1300 | M1300_PI01 M1300_PI02 |  | M1300_PI0102_Loc | = | 0 |  | 0 |  | 0 | Pipe location: 0=External 1=Internal 2=Buried |  | 1 | V001
M1300 | M1300_PI01 M1300_PI02 |  | M1300_PI01_Di | = | 0.32271 |  | 0.32271 | m | MAX(0.0150*(M1300_PU01_M/M1300_RoPri)^0.5,0.012) | Inside diameter |  | 1 | V001
M1300 | M1300_PI01 M1300_PI02 |  | M1300_PI01_e | = | 0.0075609 |  | 0.0075609 | m | ((1000*M1300_PI01_Di)*0.01823616+1.67597866)/1000 | Pipe thickness. Based on tabulated data, a linear correlation is obtained by using the polyfit function in the python program. For more information, see annexes. |  | 1 | V001
M1300 | M1300_PI01 M1300_PI02 |  | M1300_PI01_Do | = | 0.33783 |  | 0.33783 | m | M1300_PI01_Di+2*M1300_PI01_e | Outside diameter |  | 1 | V001
M1300 | M1300_PI01 M1300_PI02 |  | M1300_PI01_Kpi | = | 1180.8 |  | 1180.8 | kJ/h.m.K | 328*WTOKJPH | Pipe thermal conductivity |  | 1 | V001
M1300 | M1300_PI01 M1300_PI02 |  | M1300_PI01_Insth | = | 0.059731 |  | 0.059731 | m | ((1000*M1300_PI01_Do)*0.0253172213+51.1780361)/1000 | Insulation thickness. Based on tabulated data, a linear correlation is obtained by using the polyfit function in the python program. For more information, see annexes. |  | 1 | V001
M1300 | M1300_PI01 M1300_PI02 |  | M1300_PI01_Insk | = | 0.1548 |  | 0.1548 | kJ/h.m.K | 0.043*WTOKJPH | Conductivity of insulation |  | 1 | V001
M1300 | M1300_PI01 M1300_PI02 |  | M1300_PI01_L | = | 712.0224 |  | 712.0224 | m | 3*(M1300_WSS01_Area*3)^0.5 | Total pipe length. Forward and Return. | Level#2 | 1 | V001
M1300 | M1300_PI01 M1300_PI02 |  | M1300_PI01_L2 | = | 356.0112 |  | 356.0112 | m | 0.5*M1300_PI01_L | Pipe length oneway. |  | 1 | V001
M1300 |  | * | HEAT EXCHANGER PARAMETERS
M1300 |  |  | EQUATION | 3 | [7 empty] | 1 | V001
M1300 | M1300_HX01 |  | M1300_HX01_DTLM | = | 4 |  | 4 | °C | 4 | DTLM of the primary heat exchanger | Level#2 | 1 | V001
M1300 | M1300_HX01 |  | M1300_Qmax_solar | = | 46992708.3492 |  | 46992708.3492 | kJ/h | M1300_WSS01_Area*Itmax*M1300_WSS01_a0 | Total maximum solar power equal to Itmax * Area * collector intercept efficiency |  | 1 | V001
M1300 | M1300_HX01 |  | M1300_HX01_UA | = | 11748177.0873 |  | 11748177.0873 | kJ/h.°C | M1300_Qmax_solar/M1300_HX01_DTLM | UA parameter associated with the primary heat exchanger |  | 1 | V001
M1300 |  | * | PUMP PARAMETERS
M1300 |  |  | EQUATION | 9 | [7 empty] | 1 | V001
M1300 | M1300_PU01 |  | M1300_PU01_MMin | = | 0 |  | 0 | kg/h | M1300_WSS01_CtFRMin*M1300_PU01_M | Minimum mass flow rate of pump |  | 1 | V001
M1300 | M1300_PU01 |  | M1300_PU01_M | = | 469422.1422 |  | 469422.1422 | kg/h | M1300_WSS01_MPAC*M1300_WSS01_Area | Nominal pump mass flow rate |  | 1 | V001
M1300 | M1300_PU01 |  | M1300_PU01_V | = | 462.8401 |  | 462.8401 | m3/h | M1300_PU01_M/M1300_RoPri | Pump flow rate |  | 1 | V001
M1300 | M1300_PU01 |  | M1300_PU01_AP | = | 298180.9446 |  | 298180.9446 | Pa | MIN(GT(M1300_PU01_V,0.2)*((9.49779473*10**-6)*M1300_PU01_V**3-0.00350971*M1300_PU01_V**2+0.44274642*M1300_PU01_V+5.87642027)+LE(M1300_PU01_V,0.2)*25*M1300_PU01_V,30)*M1300_RoPri*9.8 | Nominal pressure difference |  | 1 | V001
M1300 | M1300_PU01 |  | M1300_PU01_P | = | 197157.2997 |  | 197157.2997 | kJ/h | M1300_PU01_AP*M1300_PU01_V*(1/3600)*3.6/eta_pump | Rated power consumption |  | 1 | V001
M1300 | M1300_PU02 |  | M1300_PU02_M | = | 435897.1107 |  | 435897.1107 | kg/h | M1300_PU01_M*M1300_CpPri/M1300_CpSec | Rated flow rate |  | 1 | V001
M1300 | M1300_PU02 |  | M1300_PU02_V | = | 435.8971 |  | 435.8971 | m3/h | M1300_PU02_M/M1300_RoSec | Pump flow rate |  | 1 | V001
M1300 | M1300_PU02 |  | M1300_PU02_AP | = | 294000 |  | 294000 | Pa | MIN(GT(M1300_PU02_V,0.2)*((9.49779473*10**-6)*M1300_PU02_V**3-0.00350971*M1300_PU02_V**2+0.44274642*M1300_PU02_V+5.87642027)+LE(M1300_PU02_V,0.2)*25*M1300_PU02_V,30)*M1300_RoSec*9.8 | Nominal pressure difference |  | 1 | V001
M1300 | M1300_PU02 |  | M1300_PU02_P | = | 183076.7865 |  | 183076.7865 | kJ/h | M1300_PU02_AP*M1300_PU02_V*(1/3600)*3.6/eta_pump | Rated power consumption |  | 1 | V001
M1300 |  | * | CONTROL PARAMETERS
M1300 |  |  | EQUATION | 8 | [7 empty] | 1 | V001
M1300 | M1300_CON01 |  | M1300_CON01_GTHb | = | 137.9286 |  | 137.9286 | W/m2 | M1300_CON01_GTLb+50 |  |  | 1 | V001
M1300 | M1300_CON01 |  | M1300_CON01_SRadGTH | = | 496.5429 |  | 496.5429 | kJ/h.m2 | M1300_CON01_GTHb*WTOKJPH | Upper dead band. Radiation control |  | 1 | V001
M1300 | M1300_CON01 |  | M1300_CON01_GTLb | = | 87.9286 |  | 87.9286 | W/m2 | (M1300_WSS01_a1/WTOKJPH*(M1300_WSS01_TCol_est-20*PAR_REN-TAirAve)+M1300_WSS01_a2/WTOKJPH*(M1300_WSS01_TCol_est-20*PAR_REN-TAirAve)^2)/M1300_WSS01_a0 |  | Level#2 | 1 | V001
M1300 | M1300_CON01 |  | M1300_CON01_SRadGTL | = | 316.5429 |  | 316.5429 | kJ/h.m2 | M1300_CON01_GTLb*WTOKJPH | Lower dead band. Radiation control |  | 1 | V001
M1300 | M1300_CON02 |  | M1300_CON02_DifDelTL | = | 4 |  | 4 | °C | M1300_HX01_DTLM | Lower dead band. Temperature control |  | 1 | V001
M1300 | M1300_CON02 |  | M1300_CON02_DifDelTH | = | 6 |  | 6 | °C | M1300_CON02_DifDelTL+2 | Upper dead band. Temperature control |  | 1 | V001
M1300 | M1300_WSS01 |  | M1300_WSS01_Tmax | = | 140 |  | 140 | °C | 140 | High limit cut-out | Level#1 | 1 | V001
M1300 | M1300_CON02 |  | M1300_CON02_TST1Max | = | 115 |  | 115 | °C | max(90,TDemSetpar+20) | High limit cut-out | Level#1 | 1 | V001
MACROS EXTERNAS DE WEDISTRICT
M0000 |  | * | LOGICAL UNIT ASSIGN
|  |  | !Meteo | 10-89 | [7 empty] | 1
|  |  | !Mascaras | 90-99 | [7 empty] | 1
|  |  | !WESSUN | 100-129 | [7 empty] | 1
|  |  | !PTC | 130-139 | [7 empty] | 1
|  |  | !Fresnel | 140-149 | [7 empty] | 1
|  |  | !Calderas | 300-399 | [7 empty] | 1
|  |  | !Chillers | 400-499 | [7 empty] | 1
|  |  | !Demandas | 800-899 | [7 empty] | 1
|  |  | !Outputs | 900-999 | [7 empty] | 1
M0000 |  |  | EQUATION | 5 | [7 empty] | 1 | V001
M0000 | M1300 |  | ONLINE | = | 0 |  | 0 | - | 0 | Shut off Online w/o removing |  | 1 | V001
M0000 | M1300 |  | M0100_LU_MET | = | 14 |  | 14 | - | EQL(PAR_LOC,1)*11+EQL(PAR_LOC,2)*12+EQL(PAR_LOC,3)*13+EQL(PAR_LOC,4)*14+EQL(PAR_LOC,5)*15+EQL(PAR_LOC,6)*16 | Logical unit for location | Level#1Ext.File Location | 1 | V001
M0000 | M1300 |  | M1300_LU_MSK | = | 90 |  | 90 | - | 90 | Logical unit for data file |  | 1 | V001
M0000 | M1300 |  | M1300_LU_COL | = | 48 |  | 48 | - | (EQL(PAR_STC,1)+EQL(PAR_STC,2))*103+EQL(PAR_STC,3)*103+EQL(PAR_STC,4)*104+EQL(PAR_STC,5)*105+EQL(PAR_STC,6)*106+EQL(PAR_STC,7)*107 | Logical unit for solar collector technology | Level#1Ext.File Collector | 1 | V001
M0000 | M1300 |  | M8100_LU_DEM | = | 801 |  | 801 | - | 801 | Logical unit for input file |  | 1 | V001
M0000 |  | * | LOCATION AND METEO PARAMETERS
M0000 |  |  | EQUATION | 12 | [7 empty] | 1 | V001
M0000 | M1300 |  | Type_Meteofile | = | 2 |  | 2 | TMY2 | 2 | The type of file which is to be read: 1 = TMY format, 2 = TMY2 format, 3 = Energy+ format, 4 = IWEC format, 5 = CWEC format, 6=Metoenorm for TRNSYS format, 7 = TMY3 format, 8 = German TRY 2004 format, 8 = German TRY 2010 format |  | 1 | V001
M0000 | M1300 |  | Mode_TiltSurf | = | 1 |  | 1 | TMY2 | 1 | The radiation processing mode that will be used to calculate the radiation components on a tilted surface: 1= Isotropic Sky Model, 2 = Hay and Davies Model, 3 = Reindl Model, 4 = Perez 1988 Model. 5 = Perez 1999 Model. Refer to the documentation for the Type 16 model for more information. |  | 1 | V001
M0000 | M1300 |  | PAR_LOC | = | 4 |  | 4 |  | 4 |  | Level#1Ext.File Location | 1 | V001
M0000 | M1300 |  | Gth | = | 1661.53 |  | 1661.53 | kWh/m2 | EQL(PAR_LOC,1)*988.27+EQL(PAR_LOC,2)*1143.27+EQL(PAR_LOC,3)*1443.75+EQL(PAR_LOC,4)*1661.53+EQL(PAR_LOC,5)*1843.28+EQL(PAR_LOC,6)*2359.84 | The total radiation (beam + diffuse) incident upon a horizontal surface. ### Only used for pre-sizing WESSUN collector area ###. | Level#1Ext.File Location | 1 | V001
M0000 | M1300 |  | Gbh | = | 1008.62 |  | 1008.62 | kWh/m2 | EQL(PAR_LOC,1)*436.11+EQL(PAR_LOC,2)*482.44+EQL(PAR_LOC,3)*731.47+EQL(PAR_LOC,4)*1008.62+EQL(PAR_LOC,5)*1206.82+EQL(PAR_LOC,6)*1677.30 | The beam radiation incident upon a horizontal surface. ### Only used for pre-sizing WESSUN collector area ###. | Level#1Ext.File Location | 1 | V001
M0000 | M1300 |  | Gdh | = | 652.91 |  | 652.91 | kWh/m2 | Gth-Gbh | The diffuse radiation incident upon a horizontal surface. ### Only used for pre-sizing WESSUN collector area ###. |  | 1 | V001
M0000 | M1300 |  | Itmax | = | 3960 |  | 3960 | kJ/h.m2 | 1100*WTOKJPH !kJ/h.m2 (EQL(PAR_LOC,1)*1100+EQL(PAR_LOC,2)*1050+EQL(PAR_LOC,3)*1050+EQL(PAR_LOC,4)*1000+EQL(PAR_LOC,5)*1000)*WTOKJPH | Máximum global solar radiation on a normal-to-sun surface. Used in sizing solar power. | Level#1Ext.File Location | 1 | V001
M0000 | M1300 |  | Itnom | = | 668.48 |  | 668.48 | W/m2 | EQL(PAR_LOC,1)*511.03+EQL(PAR_LOC,2)*537.89+EQL(PAR_LOC,3)*604.22+EQL(PAR_LOC,4)*668.48+EQL(PAR_LOC,5)*718.02+EQL(PAR_LOC,6)*861.92 | The mean (average) global radiation during sunny days throughout the year. ### Only used for pre-sizing WESSUN collector area ###. | Level#1Ext.File Location | 1 | V001
M0000 | M1300 |  | Lat | = | 40.4167 |  | 40.4167 | ° | EQL(PAR_LOC,1)*55.6667+EQL(PAR_LOC,2)*46.9833+EQL(PAR_LOC,3)*41.3879+EQL(PAR_LOC,4)*40.4167+EQL(PAR_LOC,5)*-33.4667+EQL(PAR_LOC,6)*-22.3094 | Location latitude | Level#1Ext.File Location | 1 | V001
M0000 | M1300 |  | TAirAve | = | 13.91 |  | 13.91 | °C | EQL(PAR_LOC,1)*7.99+EQL(PAR_LOC,2)*8.41+EQL(PAR_LOC,3)*16.27+EQL(PAR_LOC,4)*13.91+EQL(PAR_LOC,5)*14.01+EQL(PAR_LOC,6)*11.85 | The mean (average) temperature during the year. Used in ground temperature estimation and for ### pre-sizing WESSUN collector area ###. | Level#1Ext.File Location | 1 | V001
M0000 | M1300 |  | ATAir | = | 35 |  | 35 | °C | 35 | The amplitude of the anual temperature throughout the year. Used in ground temperature estimation. |  | 1 | V001
M0000 | M1300 |  | TAirTime | = | 222 |  | 222 |  | GT(Lat,0)*222+LT(Lat,0)*42 | Time shift (in days) between the beginning of the calendar year and the occurence of the minimum surface temperature. Used in ground temperature estimation. Correlation relates to south or north hemisphere. |  | 1 | V001
M0000 |  | * | GENERAL PARAMETERS
M0000 |  |  | EQUATION | 16 | [7 empty] | 1 | V001
M0000 | M1300 |  | KJPHtokW | = | 0.00027778 |  | 0.00027778 | W to kJ/h | 0.00027778 | Conversion from kJ/h to kW |  | 1 | V001
M0000 | M1300 |  | KJPHtoMW | = | 2.7778e-07 |  | 2.7778e-07 | W to kJ/h | 2.7778e-07 | Conversion from kJ/h to MW |  | 1 | V001
M0000 | M1300 |  | WTOKJPH | = | 3.6 |  | 3.6 | W to kJ/h | 3.6 | Conversion from W to kJ/h |  | 1 | V001
M0000 | M1300 |  | GrRef | = | 0.2 |  | 0.2 | - | 0.2 | Ground reflectance |  | 1 | V001
M0000 | M1300 |  | PI | = | 3.1416 |  | 3.1416 | - | 3.1416 | PI Value |  | 1 | V001
M0000 | M1300 |  | eta_pump | = | 0.7 |  | 0.7 | - | 0.7 | Hydraulic efficiency |  | 1 | V001
M0000 | M1300 |  | TCOLDW | = | 13.91 |  | 13.91 | °C | TAirAve | Initial fluid temperature. Assumed mean location ambient temperature. |  | 1 | V001
M0000 | M1300 |  | CpAgua | = | 4.19 |  | 4.19 | kJ/kg.K | 4.19 | Fluid specific heat (water) |  | 1 | V001
M0000 | M1300 |  | RoAgua | = | 1000 |  | 1000 | kg/m3 | 1000 | Fluid density (water) |  | 1 | V001
M0000 | M1300 |  | MuAgua | = | 1.8 |  | 1.8 | kg/m.h | 3600*0.0005 | Fluid viscosity (water) |  | 1 | V001
M0000 | M1300 |  | Kagua | = | 2.34 |  | 2.34 | kJ/h.m.K | 3.6*0.65 | Fluid thermal conductivity (water) |  | 1 | V001
M0000 | M1300 |  | IntSurConvCoef | = | 6 |  | 6 | kJ/h.m2.K | 6 | Indoor convection coefficient |  | 1 | V001
M0000 | M1300 |  | ExtSurConvCoef | = | 13 |  | 13 | kJ/h.m2.K | 13 | Outdoor convection coefficient |  | 1 | V001
M0000 | M1300 |  | SoilCond | = | 8.72 |  | 8.72 | kJ/h.m.K | 8.72 | Soil thermal conductivity |  | 1 | V001
M0000 | M1300 |  | SoilDensity | = | 3200 |  | 3200 | kg/m3 | 3200 | Soil density |  | 1 | V001
M0000 | M1300 |  | SoilCp | = | 0.84 |  | 0.84 | kJ/kg.K | 0.84 | Soil specific heat |  | 1 | V001
M1300 VALIDATION (NOT USED IN COMMON WE DISTRICT STRUCTURE)
|  | * | PARAMETRIC TABLE SIMULATION PARAMETERS
|  |  | EQUATION | 3 | [7 empty] | 1
|  |  | PAR_QDE | = | 1 |  | 1 | - | 1 | Demand factor |  | 1
|  |  | PAR_TDE | = | 85 |  | 85 | °C | 85 | Return temperature |  | 1
|  |  | PAR_REN | = | 0.5 |  | 0.5 | % | 0.5 | Used for pre-sizing |  | 1
|  | * | DEMAND PARAMETERS
|  |  | EQUATION | 4 | [7 empty] | 1
|  |  | QDEMMAND | = | 40000000 |  | 40000000 | kWh | 40000*10^3 | Used for pre-sizing |  | 1
|  |  | QDEM_MAX | = | 11200 |  | 11200 | kW | 11200 | Maximum demand |  | 1
|  |  | TDemSetpar | = | 95 |  | 95 | °C | PAR_TDE+10 | Supply temperature |  | 1
|  |  | TDemRetpar | = | 85 |  | 85 | °C | PAR_TDE | Return temperature |  | 1
|  | * | MAIN PREDIM PARAMETERS
|  |  | EQUATION | 3 | [7 empty] | 1
|  |  | EFF_SST | = | 0.48346 |  | 0.48346 | - | EFF_STO*M1300_EFF_COL |  |  | 1
|  |  | EFF_STO | = | 0.9 |  | 0.9 | - | 0.9 |  |  | 1
|  |  | VolPA | = | 150 |  | 150 |  | 150 | Accumulation volumen of the thermal storage system |  | 1
|  | * | GENERAL PARAMETERS
|  |  | EQUATION | 1 | [7 empty] | 1
|  |  | CpTer | = | 3.9 |  | 3.9 | kJ/kg.K | 3.9 |  |  | 1
|  | * | PIPE PARAMETERS
|  |  | EQUATION | 8 | [7 empty] | 1
|  |  | SSY_Pi5Di | = | 0.52089 |  | 0.52089 | m | MAX(0.015*(SSY_HX2FRmax/M1300_RoSec)^0.5,0.012) | Inside diameter |  | 1
|  |  | ePi5 | = | 0.011175 |  | 0.011175 | m | ((1000*SSY_Pi5Di)*0.01823616+1.67597866)/1000 | Pipe thickness |  | 1
|  |  | SSY_Pi5Do | = | 0.54324 |  | 0.54324 | m | SSY_Pi5Di+2*ePi5 | Outside diameter |  | 1
|  |  | SSY_Pi5KPi | = | 1180.8 |  | 1180.8 | kJ/h.m.K | 328*WTOKJPH | Pipe thermal conductivity |  | 1
|  |  | SSY_Pi5Insth | = | 0.051192 |  | 0.051192 | m | ((SSY_Pi5Do)*0.0253172213+51.1780361)/1000 | Insulation thickness |  | 1
|  |  | SSY_Pi5Insk | = | 0.1548 |  | 0.1548 | kJ/h.m.K | 0.043*WTOKJPH | Conductivity of insulation |  | 1
|  |  | SSY_Pi5L | = | 0.001 |  | 0.001 | m | 0.001 | Total pipe length |  | 1
|  |  | SSY_Pi5L2 | = | 0.0005 |  | 0.0005 | m | 0.5*SSY_Pi5L | Pipe length |  | 1
|  | * | HEAT EXCHANGER PARAMETERS
|  |  | EQUATION | 3 | [7 empty] | 1
|  |  | Qmax_demanda | = | 40320000 |  | 40320000 | kJ/h | QDEM_MAX*1000*WTOKJPH |  |  | 1
|  |  | SSY_HX02_DTLM | = | 4 |  | 4 | °C | 4 | Design difference temperature between the cold inlet water temperature and the hot outlet temperature |  | 1
|  |  | SSY_HX2UA | = | 10080000 |  | 10080000 | kJ/h.ºC | Qmax_demanda/SSY_HX02_DTLM | Overall heat transfer coefficient of exchanger |  | 1
|  | * | PUMP PARAMETERS
|  |  | EQUATION | 4 | [7 empty] | 1
|  |  | SSY_HX2FRmax | = | 1033846.1538 |  | 1033846.1538 | kg/h | Qmax_demanda/CpTer/(TDemSetpar-TDemRetpar) | Maximum flowrate in hot side |  | 1
|  |  | SSY_HX2FRmin | = | 0 |  | 0 | kg/h | SSY_HX2FRmax*0.0 | Minimum flow rate in hot side |  | 1
|  |  | M1300_PU03_AP | = | 100 |  | 100 | KPa | 100 | Pressure difference |  | 1
|  |  | SSY_Pu3P | = | 170454.2986 |  | 170454.2986 | kJ/h | SSY_HX2FRmax*M1300_PU03_AP/10*9.81/.85/.7/1000 | Maximum power |  | 1
|  | * | STORAGE PARAMETERS
|  |  | EQUATION | 33 | [7 empty] | 1
|  |  | SSY_ST1_Loc | = | 0 |  | 0 | - | 0 |  |  | 1
|  |  | SSY_ST1_Nodes | = | 10 |  | 10 | - | 10 | Number of tank nodes |  | 1
|  |  | SSY_ST1_Vol | = | 2816.5329 |  | 2816.5329 | m3 | VolPA*M1300_WSS01_Area/1000 | Tank volume |  | 1
|  |  | SSY_ST1_Height | = | 4 |  | 4 | m | 4 | Tank height |  | 1
|  |  | SSY_ST1_Fluidcp | = | 4.19 |  | 4.19 | kJ/kg.K | CpAgua | Fluid specific heat |  | 1
|  |  | SSY_ST1_Fluidrho | = | 1000 |  | 1000 | kg/m3 | RoAgua | Fluid density |  | 1
|  |  | SSY_ST1_Fluidmu | = | 1.8 |  | 1.8 | kg/m.hr | MuAgua | Fluid viscosity |  | 1
|  |  | SSY_ST1_Fluidk | = | 2.34 |  | 2.34 | hr.m.K | KAgua | Fluid thermal conductivity |  | 1
|  |  | SSY_ST1_IsoTopTh | = | 0.03096 |  | 0.03096 | m | 0.043*3.6/5 | Top insulation thickness |  | 1
|  |  | SSY_ST1_IsoTopK | = | 0.043 |  | 0.043 | W.m.K | 0.043 | Top thermal conductivity |  | 1
|  |  | SSY_ST1_IsoLatTh | = | 0.03096 |  | 0.03096 | m | 0.043*3.6/5 | Edge insulation thickness |  | 1
|  |  | SSY_ST1_IsoLatK | = | 0.043 |  | 0.043 | W.m.K | 0.043 | Edge thermal conductivity |  | 1
|  |  | SSY_ST1_IsoBotTh | = | 0.03096 |  | 0.03096 | m | 0.043*3.6/5 | Bottom insulation thickness |  | 1
|  |  | SSY_ST1_IsoBotK | = | 0.043 |  | 0.043 | W.m.K | 0.043 | Bottom thermal conductivity |  | 1
|  |  | SSY_ST1_Utop | = | 5 |  | 5 | kJ/hr.m^2.K | SSY_ST1_IsoTopK*WTOKJPH/SSY_ST1_IsoTopTh | Top loss coefficient |  | 1
|  |  | SSY_ST1_Ulat | = | 5 |  | 5 | kJ/hr.m^2.K | SSY_ST1_IsoLatK*WTOKJPH/SSY_ST1_IsoLatTh | Edge Loss Coefficient |  | 1
|  |  | SSY_ST1_Ubot | = | 5 |  | 5 | kJ/hr.m^2.K | SSY_ST1_IsoBotK*WTOKJPH/SSY_ST1_IsoBotTh | Bottom Loss Coefficient |  | 1
|  |  | SSY_ST1_P1Mode | = | 1 |  | 1 |  | 1 | Inlet Flow Mode-1 |  | 1
|  |  | SSY_ST1_P1In | = | 1 |  | 1 |  | 1 | Entry Node-1 |  | 1
|  |  | SSY_ST1_P1Ou | = | 10 |  | 10 |  | 10 | Exit Node-1 |  | 1
|  |  | SSY_ST1_P2Mode | = | 1 |  | 1 |  | 1 | Inlet Flow Mode-2 |  | 1
|  |  | SSY_ST1_P2In | = | 10 |  | 10 |  | 10 | Entry Node-2 |  | 1
|  |  | SSY_ST1_P2Ou | = | 1 |  | 1 |  | 1 | Exit Node-2 |  | 1
|  |  | SSY_ST1_P3Mode | = | 1 |  | 1 |  | 1 | Inlet Flow Mode-3 |  | 1
|  |  | SSY_ST1_P3In | = | 10 |  | 10 |  | 10 | Entry Node-3 |  | 1
|  |  | SSY_ST1_P3Ou | = | 1 |  | 1 |  | 1 | Exit Node-3 |  | 1
|  |  | SSY_ST1_P4Mode | = | 1 |  | 1 |  | 1 | Inlet Flow Mode-4 |  | 1
|  |  | SSY_ST1_P4In | = | 10 |  | 10 |  | 10 | Entry Node-4 |  | 1
|  |  | SSY_ST1_P4Ou | = | 1 |  | 1 |  | 1 | Exit Node-4 |  | 1
|  |  | SSY_ST1_P5Mode | = | 1 |  | 1 |  | 1 | Inlet Flow Mode-5 |  | 1
|  |  | SSY_ST1_P5In | = | 10 |  | 10 |  | 10 | Entry Node-5 |  | 1
|  |  | SSY_ST1_P5Ou | = | 1 |  | 1 |  | 1 | Exit Node-5 |  | 1
|  |  | SSY_ST1_Tt0 | = | 85 |  | 85 |  | TDemRetpar | Initial Tank Temperature |  | 1
|  | * | CONTROL PARAMETERS
|  |  | EQUATION | 2 | [7 empty] | 1
M1300 |  |  | Ct2DifDelTL | = | 2 |  | 2 | °C | 2 | Lower dead band |  | 1
M1300 |  |  | Ct2DifDelTH | = | 6 |  | 6 | °C | M1300_CON02_DifDelTL+2 | Upper dead band |  | 1

## ficheroM1300
*FLUID PARAMETERS
EQUATION 9
M1300_PriAntifree = 30 !%
M1300_CpPri = (4.185-M1300_PriAntifree*0.9808/100) !kJ/kg.K
M1300_RoPri = (1000+47.403*M1300_PriAntifree/100) !kg/m3
M1300_MuPri = 3600*(0.0005+0.0008*M1300_PriAntifree/100+0.0019*(M1300_PriAntifree/100)^2) !kg/m.h
M1300_KPri = 2.2 !kJ/h.m.K
M1300_CpSec = CpAgua !kJ/kg.K
M1300_RoSec = RoAgua !kg/m3
M1300_MuSec = MuAgua !kg/m.h
M1300_KSec = Kagua !kJ/h.m.K
*HORIZON AND ARRAY SHADOW PARAMETERS
EQUATION 9
M1300_MSK_NumAngles = 16 !-
M1300_GrHrAzimuth = 0 !°
M1300_GrHrSlope = 0 !°
M1300_WSSHeightShadow = M1300_COL01_Cheight+(EQL(PAR_STC,4)+EQL(PAR_STC,7)) !m
M1300_WSSSlopeShadow = M1300_ColHrSlope+0.001 !°
*M1300_WSS01_GndUsability M1300_WSS01_Cheight*COS(M1300_ColHrSlope)/M1300_WSSRowSep*1 !-
*M1300_COL01_GndUsability M1300_WSS01_Cheight/M1300_WSSRowSep !-
M1300_WSS01_Cheight = (EQL(PAR_STC,1)*2.191+EQL(PAR_STC,2)*2.224+EQL(PAR_STC,3)*3.0736+EQL(PAR_STC,4)*3.9231+EQL(PAR_STC,5)*2.427+EQL(PAR_STC,6)*3.2789+EQL(PAR_STC,7)*4.1332) !-
M1300_WSSRowLen = MAX(60,(3*M1300_WSS01_Area)^0.5) !m
M1300_WSSNRows = M1300_WSS01_Area/M1300_WSSRowLen !-
M1300_WSSRowSep = (1+0.25*NOT(EQL(M1300_ColHrSlope,0))+0.25*(MIN(90,ABS(M1300_ColHrAzimuth))/90))*(M1300_WSSHeightShadow)*(COS(M1300_ColHrSlope)+SIN(M1300_ColHrSlope)/TAN(90-ABS(Lat)-23.5)) !m
*COLLECTOR PARAMETERS
EQUATION 37
PAR_STC = 6 !-
PAR_KSOIL = 0 !-
PAR_fRedDifusa = 0.8 !-
M1300_WSS01_TCol_est = (TDemSetpar+TDemRetpar)*0.5+M1300_HX01_DTLM+15*PAR_REN !°C
M1300_EFF_COL = MAX(0.3,M1300_WSS01_a0-M1300_WSS01_a1/WTOKJPH*(M1300_WSS01_TCol_est-TAirAve)/Itnom-M1300_WSS01_a2/WTOKJPH*(M1300_WSS01_TCol_est-TAirAve)^2/Itnom) !%
M1300_WSS01_Area = 0.75*QDEMMAND*PAR_REN/(((Gbh+Gdh/M1300_WSS01_C)*COS(ABS(Lat)-M1300_ColHrSlope))*M1300_EFF_COL) !m2
M1300_ColHrSlope = 45 !°
M1300_ColHrAzimuth = M1300_GrHrAzimuth !°
M1300_COL01_Mode = (EQL(PAR_STC,1)+EQL(PAR_STC,2))*1+(EQL(PAR_STC,3)+EQL(PAR_STC,4)+EQL(PAR_STC,5)+EQL(PAR_STC,6)+EQL(PAR_STC,7))*2 ! !-
M1300_WSS01_Nserie = MIN(M1300_WSS01_Ncol,2) !-
M1300_WSS01_Nparalel = M1300_WSS01_Ncol/M1300_WSS01_Nserie !-
M1300_WSS01_Acol = (EQL(PAR_STC,1)*2.52+EQL(PAR_STC,2)*12.13+EQL(PAR_STC,3)*16.764+EQL(PAR_STC,4)*21.397+EQL(PAR_STC,5)*4.46+EQL(PAR_STC,6)*6.025+EQL(PAR_STC,7)*7.595) !m2
M1300_WSS01_Ncol = M1300_WSS01_Area/(M1300_WSS01_Acol) !-
M1300_COL01_Cheight = (EQL(PAR_STC,1)*2.191+(EQL(PAR_STC,2)+EQL(PAR_STC,3)+EQL(PAR_STC,4))*2.224+(EQL(PAR_STC,5)+EQL(PAR_STC,6)+EQL(PAR_STC,7))*2.427) !m2
M1300_WSS01_TestMode = 2 !-
M1300_WSS01_ThCap = M1300_WSS01_ThCapUn*M1300_WSS01_Area/M1300_WSS01_C !kJ/K
M1300_WSS01_ThCapUn = (0.4*M1300_CpPri+0.2*9*0.82+5*0.385) !kJ/K.m2
M1300_WSS01_Reflec = 0.94 !%
M1300_WSS01_C = ((EQL(PAR_STC,1)+EQL(PAR_STC,2)+EQL(PAR_STC,5))*1+EQL(PAR_STC,3)*1.382+EQL(PAR_STC,4)*1.764+EQL(PAR_STC,6)*1.351+EQL(PAR_STC,7)*1.703) !-
M1300_COL01_a0 = EQL(PAR_STC,1)*0.761+(EQL(PAR_STC,2)+EQL(PAR_STC,3)+EQL(PAR_STC,4))*0.857+(EQL(PAR_STC,5)+EQL(PAR_STC,6)+EQL(PAR_STC,7))*0.642 !-
M1300_WSS01_a0 = M1300_COL01_a0*(1-PAR_KSOIL)*(1+M1300_WSS01_Reflec*(M1300_WSS01_C-1))/M1300_WSS01_C !-
M1300_COL01_a1 = (EQL(PAR_STC,1)*3.711+(EQL(PAR_STC,2)+EQL(PAR_STC,3)+EQL(PAR_STC,4))*3.083+(EQL(PAR_STC,5)+EQL(PAR_STC,6)+EQL(PAR_STC,7))*0.89) !W/m2.K
M1300_WSS01_a1 = M1300_COL01_a1/M1300_WSS01_C*WTOKJPH !kJ/h.m2.K
M1300_COL01_a2 = (EQL(PAR_STC,1)*0.014+(EQL(PAR_STC,2)+EQL(PAR_STC,3)+EQL(PAR_STC,4))*0.013+(EQL(PAR_STC,5)+EQL(PAR_STC,6)+EQL(PAR_STC,7))*0.001) !W/m2.K2
M1300_WSS01_a2 = M1300_COL01_a2/M1300_WSS01_C*WTOKJPH !kJ/h.m2.k2
M1300_WSS01_Mtest = 50 !kg/h
M1300_COL01_IAMK50 = EQL(PAR_STC,1)*0.91+EQL(PAR_STC,2)*0.91+(EQL(PAR_STC,3)+EQL(PAR_STC,4)+EQL(PAR_STC,5)+EQL(PAR_STC,6)+EQL(PAR_STC,7))*1 !-
M1300_COL01_IAM1 = MAX(0,(1-M1300_COL01_IAMK50)*COS(50)/(1-COS(50))) !-
M1300_COL01_IAM2 = 0 !-
M1300_WSS01_DataTrans = 35 !-
M1300_WSS01_DataLong = 13 !-
M1300_WSS01_CtFRMin = 0 !kg/h
M1300_WSS01_MPAC = M1300_WSS01_MTest/M1300_WSS01_Nserie !kg/h.m2
M1300_WSS01_Control = 0 !-
M1300_WSS01_Tset = TDemSetpar + M1300_HX01_DTLM + 2 !°C
*PIPE PARAMETERS
EQUATION 9
M1300_PI0102_Loc = 0 !
M1300_PI01_Di = MAX(0.0150*(M1300_PU01_M/M1300_RoPri)^0.5,0.012) !m
M1300_PI01_e = ((1000*M1300_PI01_Di)*0.01823616+1.67597866)/1000 !m
M1300_PI01_Do = M1300_PI01_Di+2*M1300_PI01_e !m
M1300_PI01_Kpi = 328*WTOKJPH !kJ/h.m.K
M1300_PI01_Insth = ((1000*M1300_PI01_Do)*0.0253172213+51.1780361)/1000 !m
M1300_PI01_Insk = 0.043*WTOKJPH !kJ/h.m.K
M1300_PI01_L = 3*(M1300_WSS01_Area*3)^0.5 !m
M1300_PI01_L2 = 0.5*M1300_PI01_L !m
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
*HEAT EXCHANGER PARAMETERS
EQUATION 3
M1300_HX01_DTLM = 4 !°C
M1300_Qmax_solar = M1300_WSS01_Area*Itmax*M1300_WSS01_a0 !kJ/h
M1300_HX01_UA = M1300_Qmax_solar/M1300_HX01_DTLM !kJ/h.°C
*PUMP PARAMETERS
EQUATION 9
M1300_PU01_MMin = M1300_WSS01_CtFRMin*M1300_PU01_M !kg/h
M1300_PU01_M = M1300_WSS01_MPAC*M1300_WSS01_Area !kg/h
M1300_PU01_V = M1300_PU01_M/M1300_RoPri !m3/h
M1300_PU01_AP = MIN(GT(M1300_PU01_V,0.2)*((9.49779473*10**-6)*M1300_PU01_V**3-0.00350971*M1300_PU01_V**2+0.44274642*M1300_PU01_V+5.87642027)+LE(M1300_PU01_V,0.2)*25*M1300_PU01_V,30)*M1300_RoPri*9.8 !Pa
M1300_PU01_P = M1300_PU01_AP*M1300_PU01_V*(1/3600)*3.6/eta_pump !kJ/h
M1300_PU02_M = M1300_PU01_M*M1300_CpPri/M1300_CpSec !kg/h
M1300_PU02_V = M1300_PU02_M/M1300_RoSec !m3/h
M1300_PU02_AP = MIN(GT(M1300_PU02_V,0.2)*((9.49779473*10**-6)*M1300_PU02_V**3-0.00350971*M1300_PU02_V**2+0.44274642*M1300_PU02_V+5.87642027)+LE(M1300_PU02_V,0.2)*25*M1300_PU02_V,30)*M1300_RoSec*9.8 !Pa
M1300_PU02_P = M1300_PU02_AP*M1300_PU02_V*(1/3600)*3.6/eta_pump !kJ/h
*CONTROL PARAMETERS
EQUATION 8
M1300_CON01_GTHb = M1300_CON01_GTLb+50 !W/m2
M1300_CON01_SRadGTH = M1300_CON01_GTHb*WTOKJPH !kJ/h.m2
M1300_CON01_GTLb = (M1300_WSS01_a1/WTOKJPH*(M1300_WSS01_TCol_est-20*PAR_REN-TAirAve)+M1300_WSS01_a2/WTOKJPH*(M1300_WSS01_TCol_est-20*PAR_REN-TAirAve)^2)/M1300_WSS01_a0 !W/m2
M1300_CON01_SRadGTL = M1300_CON01_GTLb*WTOKJPH !kJ/h.m2
M1300_CON02_DifDelTL = M1300_HX01_DTLM !°C
M1300_CON02_DifDelTH = M1300_CON02_DifDelTL+2 !°C
M1300_WSS01_Tmax = 140 !°C
M1300_CON02_TST1Max = max(90,TDemSetpar+20) !°C

## ficheroOTROS
*LOGICAL UNIT ASSIGN
EQUATION 5
ONLINE = 0 !-
M0100_LU_MET = EQL(PAR_LOC,1)*11+EQL(PAR_LOC,2)*12+EQL(PAR_LOC,3)*13+EQL(PAR_LOC,4)*14+EQL(PAR_LOC,5)*15+EQL(PAR_LOC,6)*16 !-
M1300_LU_MSK = 90 !-
M1300_LU_COL = (EQL(PAR_STC,1)+EQL(PAR_STC,2))*103+EQL(PAR_STC,3)*103+EQL(PAR_STC,4)*104+EQL(PAR_STC,5)*105+EQL(PAR_STC,6)*106+EQL(PAR_STC,7)*107 !-
M8100_LU_DEM = 801 !-
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
*LOCATION AND METEO PARAMETERS
EQUATION 12
PAR_LOC = 4 !
Gth = EQL(PAR_LOC,1)*988.27+EQL(PAR_LOC,2)*1143.27+EQL(PAR_LOC,3)*1443.75+EQL(PAR_LOC,4)*1661.53+EQL(PAR_LOC,5)*1843.28+EQL(PAR_LOC,6)*2359.84 !kWh/m2
Gbh = EQL(PAR_LOC,1)*436.11+EQL(PAR_LOC,2)*482.44+EQL(PAR_LOC,3)*731.47+EQL(PAR_LOC,4)*1008.62+EQL(PAR_LOC,5)*1206.82+EQL(PAR_LOC,6)*1677.30 !kWh/m2
Gdh = Gth-Gbh !kWh/m2
#REF!
Itmax = 1100*WTOKJPH !kJ/h.m2 (EQL(PAR_LOC,1)*1100+EQL(PAR_LOC,2)*1050+EQL(PAR_LOC,3)*1050+EQL(PAR_LOC,4)*1000+EQL(PAR_LOC,5)*1000)*WTOKJPH !kJ/h.m2
Itnom = EQL(PAR_LOC,1)*511.03+EQL(PAR_LOC,2)*537.89+EQL(PAR_LOC,3)*604.22+EQL(PAR_LOC,4)*668.48+EQL(PAR_LOC,5)*718.02+EQL(PAR_LOC,6)*861.92 !W/m2
Lat = EQL(PAR_LOC,1)*55.6667+EQL(PAR_LOC,2)*46.9833+EQL(PAR_LOC,3)*41.3879+EQL(PAR_LOC,4)*40.4167+EQL(PAR_LOC,5)*-33.4667+EQL(PAR_LOC,6)*-22.3094 !°
Mode_TiltSurf = 1 !TMY2
TAirAve = EQL(PAR_LOC,1)*7.99+EQL(PAR_LOC,2)*8.41+EQL(PAR_LOC,3)*16.27+EQL(PAR_LOC,4)*13.91+EQL(PAR_LOC,5)*14.01+EQL(PAR_LOC,6)*11.85 !°C
ATAir = 35 !°C
TAirTime = GT(Lat,0)*222+LT(Lat,0)*42 !
*GENERAL PARAMETERS
EQUATION 16
WTOKJPH = 3.6 !W to kJ/h
GrRef = 0.2 !-
PI = 3.141592654 !-
eta_pump = 0.7 !-
TCOLDW = TAirAve !°C
CpAgua = 4.19 !kJ/kg.K
RoAgua = 1000 !kg/m3
MuAgua = 3600*0.0005 !kg/m.h
Kagua = 3.6*0.65 !kJ/h.m.K
IntSurConvCoef = 6 !kJ/h.m2.K
ExtSurConvCoef = 13 !kJ/h.m2.K
SoilCond = 8.72 !kJ/h.m.K
SoilDensity = 3200 !kg/m3
SoilCp = 0.84 !kJ/kg.K
*PARAMETRIC TABLE SIMULATION PARAMETERS
EQUATION 3
PAR_QDE = 1 !-
PAR_TDE = 85 !°C
PAR_REN = 0.5 !%
*DEMAND PARAMETERS
EQUATION 4
QDEMMAND = 40000*10^3 !kWh
QDEM_MAX = 11200 !kW
TDemSetpar = PAR_TDE+10 !°C
TDemRetpar = PAR_TDE !°C
*MAIN PREDIM PARAMETERS
EQUATION 3
EFF_SST = EFF_STO*M1300_EFF_COL !-
EFF_STO = 0.9 !-
VolPA = 150 !
*GENERAL PARAMETERS
EQUATION 1
CpTer = 3.9 !kJ/kg.K
*PIPE PARAMETERS
EQUATION 8
SSY_Pi5Di = MAX(0.015*(SSY_HX2FRmax/M1300_RoSec)^0.5,0.012) !m
ePi5 = ((1000*SSY_Pi5Di)*0.01823616+1.67597866)/1000 !m
SSY_Pi5Do = SSY_Pi5Di+2*ePi5 !m
SSY_Pi5KPi = 328*WTOKJPH !kJ/h.m.K
SSY_Pi5Insth = ((SSY_Pi5Do)*0.0253172213+51.1780361)/1000 !m
SSY_Pi5Insk = 0.043*WTOKJPH !kJ/h.m.K
SSY_Pi5L = 0.001 !m
SSY_Pi5L2 = 0.5*SSY_Pi5L !m
*HEAT EXCHANGER PARAMETERS
EQUATION 3
Qmax_demanda = QDEM_MAX*1000*WTOKJPH !kJ/h
SSY_HX02_DTLM = 4 !°C
SSY_HX2UA = Qmax_demanda/SSY_HX02_DTLM !kJ/h.ºC
*PUMP PARAMETERS
EQUATION 4
SSY_HX2FRmax = Qmax_demanda/CpTer/(TDemSetpar-TDemRetpar) !kg/h
SSY_HX2FRmin = SSY_HX2FRmax*0.0 !kg/h
M1300_PU03_AP = 100 !KPa
SSY_Pu3P = SSY_HX2FRmax*M1300_PU03_AP/10*9.81/.85/.7/1000 !kJ/h
*STORAGE PARAMETERS
EQUATION 33
SSY_ST1_Loc = 0 !-
SSY_ST1_Nodes = 10 !-
SSY_ST1_Vol = VolPA*M1300_WSS01_Area/1000 !m3
SSY_ST1_Height = 4 !m
SSY_ST1_Fluidcp = CpAgua !kJ/kg.K
SSY_ST1_Fluidrho = RoAgua !kg/m3
SSY_ST1_Fluidmu = MuAgua !kg/m.hr
SSY_ST1_Fluidk = KAgua !hr.m.K
SSY_ST1_IsoTopTh = 0.043*3.6/5 !m
SSY_ST1_IsoTopK = 0.043 !W.m.K
SSY_ST1_IsoLatTh = 0.043*3.6/5 !m
SSY_ST1_IsoLatK = 0.043 !W.m.K
SSY_ST1_IsoBotTh = 0.043*3.6/5 !m
SSY_ST1_IsoBotK = 0.043 !W.m.K
SSY_ST1_Utop = SSY_ST1_IsoTopK*WTOKJPH/SSY_ST1_IsoTopTh !kJ/hr.m^2.K
SSY_ST1_Ulat = SSY_ST1_IsoLatK*WTOKJPH/SSY_ST1_IsoLatTh !kJ/hr.m^2.K
SSY_ST1_Ubot = SSY_ST1_IsoBotK*WTOKJPH/SSY_ST1_IsoBotTh !kJ/hr.m^2.K
SSY_ST1_P1Mode = 1 !
SSY_ST1_P1In = 1 !
SSY_ST1_P1Ou = 10 !
SSY_ST1_P2Mode = 1 !
SSY_ST1_P2In = 10 !
SSY_ST1_P2Ou = 1 !
SSY_ST1_P3Mode = 1 !
SSY_ST1_P3In = 10 !
SSY_ST1_P3Ou = 1 !
SSY_ST1_P4Mode = 1 !
SSY_ST1_P4In = 10 !
SSY_ST1_P4Ou = 1 !
SSY_ST1_P5Mode = 1 !
SSY_ST1_P5In = 10 !
SSY_ST1_P5Ou = 1 !
SSY_ST1_Tt0 = TDemRetpar !
*CONTROL PARAMETERS
EQUATION 2
Ct2DifDelTL = 2 !°C
Ct2DifDelTH = M1300_CON02_DifDelTL+2 !°C